## BFW Rotojet Failure
RCA date: | Thrusday, Oct - 25, 2018
Attendants: | M.Isa, Hendro
Problem Statement: | Failure of BFW Pump No 1 & 2
Containment Action: | COGEN Trip
Events chronology : | Sept 26th 2018 21:28 WIB BFW Pump No.2 indicating high vibration, noise and pressure & flow drop. Immediately swap to BFW No.1
Sept 27th 2018 04:29 WIB BFW Pump No.1 indicating severe leakage, high ampere and noise. BFW pump No.1 switched off and COGEN trip
Sept 27th 2018 15:00 WIB BFW Pump No.1 repaired (replace mechanical seal) and switched on for few minutes and off again due to very high vibration, noise and ampere
Sept 28th 2018 10:00 WIB BFW Pump No.2 repaired. Replaced the pump with new set.
Sept 28th 2018 22:17 COGEN running and synchronize
Facts: | BFW Pump No.2 failure coming from Pick Up tube failure causing loss of flow, pressure and vibration
BFW Pump No.1 failure coming from mech seal failure & bearing damage lead to severe leakage, high vibration, noise and ampere
Failure pick up tube BFW Pump No.2 was original parts from OEM used only from 10-sept-18
Why #1 | Why #2 | Why #3 | Why #4 | Why #5
Why both BFW Pump No.1 & 2 failure…?
1. Mechanical parts failure (bearing, rotor, mech seal, pick up tube, belt) | Why mechanical seal, bearing in BFW Pump No.1 and Pick Up Tube in BFW Pump No. 2 failure…?
Note : It was found in BFW Pump No.1 mech seal & bearing damaged. For BFW Pump No.2 was found that pick up tube failure | Note : Before BFW Pump No.2 failure, BFW pump No.1 planned to be repaired but not yet repaired due to spare parts unavailable.
1. Aging
2. Improper installation
Note : Some parts found loose (mech seal) causing leakage in BFW No.1
3. Wrong design or parts
Note : Mechanical seal and PUT sized suitable for operating condition based on manufacturer information
| 4. Fluctuation of operating condition | Why teams not have knowledge on how the operating condition affect the pump life time…?
| Note : Teams not have knowledge on how the operating condition affect the pump life time | 1. Not having enough support from Rotojet Original Manufacturer on short pick up tube lifetime.
| 5. Spare parts unavailable for BFW pump no.1 lead to BFW No.1 fail when running and COGEN trip | Why spare parts found unavailable for BFW pump no.1…?
1. shortage of spare in SSR and long delivery time when purchase the spare parts (Pick Up Tube)
2. Electrical parts failure (electric motor, MCC)
Note : No electrical parts failure found during events
Root Cause :
1. BFW fail due to failure from parts (pick up tube & mechanical seal)
Secondary Cause :
1. Spare parts unavailable during event lead to BFW back up fail
2. Not enough support from manufacturer regarding short life of pick up tube
3. Improper installation on several occasion during pump assembly
Actions :
Action Item |  | Responsible Person | Due Date | Status
1. Training of pump assembly for rotojet pump |  | Hendro. C | 2018-12-01 | Done
2. Develop SOP for rotojet assembly |  | Hendro. C | 2019-02-01 | In progress
3. Push VENDOR for better support |  | Mochamad Isa | 2019-02-01 | In progress
4. Working on rotojet spare parts |  | Purchasing